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GENERATOR OPERATING INSTRUCTION
1. Jeneratör ve motor kayışları kontrol edilerek, arızalı olanlar değiştirilir ve gevşeyenler gerdirilir.
2. Before starting the generator, thoroughly inspect all sides visually. If there are loose-ended cables, damaged hoses, broken plugs or sockets, immediately notify the electrician or the relevant personnel and ensure that there is no hazard and that there is no malfunction in the electrical panel or generator.
3. Check the generator and engine belts; replace defective belts and tighten loose belts.
4. Check the engine oil and fuel and top them up if necessary.
5. Follow the periodic and daily maintenance schedule using the maintenance card. If it is time to change the oil or filter, notify the relevant personnel and have the maintenance performed. (The engine oil and filter shall be changed every 50 operating hours.) If the generator is operated in a dusty environment, clean the cooling fins around the cylinder and check the air fan every 200 hours. Clean the air filter every 50 hours.
6. Record daily and periodic maintenance, added oil and fuel, replaced parts and daily operating hours on the designated inspection card. At the end of each month, have the card signed by the relevant supervisor, submit it, and obtain a new card.
7. After completing the above requirements, check that the switch on the generator panel is in the OFF (0) position. Start the generator in accordance with the engine operating principle, taking care to prevent the starting handle from striking anyone or anything.
8. After confirming that the generator grounding conductor is properly driven into the ground and connected at the appropriate location, open the panel switch (set it to position I) in accordance with the instructions provided by the electrician. Adjust the engine throttle until the voltmeter, ammeter and frequency meter show the appropriate values. (Adjust the engine throttle to 400 V and 50 Hz.)
9. Once the warning circuit on the generator has been adjusted, do not tamper with it in any way.
10. [bookmark: _GoBack]Do not attempt to repair even the slightest malfunction that may occur in the electrical panel, generator or engine. Notify the relevant personnel.
11. The person operating the generator shall always wear rubber gloves and rubber boots or rubber-soled safety shoes.
12. Do not connect plugs that are not suitable for the panel.
13. While the generator is operating, keep the two doors on the engine side open opposite each other. Secure the doors with their latches so that the engine can cool and malfunctions occurring during operation can be detected easily.
14. Do not draw power from the generator panel until the generator grounding conductor has been installed in a suitable wet ground location. Also ensure that equipment receiving power from the generator is properly grounded.
Record any malfunctions observed during operation and have them corrected after notifying the relevant personnel.
At the end of work, first disconnect the equipment connected to the panel, set the panel switch to the OFF (0) position, and stop the generator engine.
15. At the end of work, close and lock the generator doors to prevent unauthorized or accidental intervention by another person.
16. The generator operator shall not operate the equipment under any circumstances until they have obtained the necessary information about the electrical panel, generator and engine from the electrician and maintenance technician.
17. The generator supervisor shall carry out the required inspections and retain the records relating to those inspections.
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