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1. No one other than responsible, authorized and relevant personnel shall enter the boiler rooms.
2. Before the boilers are fired, the boiler operator shall inspect and check the condition of all valves, dampers, covers, safety valves, fuel and water quantities, and all matters related to operation.
3. Boilers shall be fired gradually and slowly during initial firing to prevent a sudden increase in temperature.
4. Before firing boilers using liquid or gaseous fuels, there shall be no spilled fuel inside the furnace, at or near the burner openings, or around the boiler. The furnace shall be thoroughly ventilated so that no explosive mixture of air, gas or fuel remains inside.
5. When putting the boilers into operation, the safety valve shall be checked before opening the main outlet valve. The air release valves on the piping system shall be kept open until all air has been discharged. After the boiler reaches the required pressure and temperature, the main outlet stop valve shall be opened gradually.
6. The boiler safety valves shall be checked at every shift change.
7. A shut-down boiler shall not be drained until its temperature and pressure have returned to normal, and the boiler operator shall continue monitoring it.
8. The boiler room shall be cleaned every day using appropriate cleaning materials.
9. Unnecessary materials, equipment, tools, or items not belonging to the installation shall not be kept in the boiler room.
10. The natural gas boiler shall be properly maintained. In the event of a malfunction, the relevant department and authorized service shall be informed.
11. If any exposed or open-ended cables are found in the boiler room, the authorized electrical technician shall be notified immediately.
12. Before firing the boiler, the water level in the system shall be checked on the hydrometer. If the water level is insufficient, water shall be added while the boiler is switched off.
13. A gas check shall be carried out. If a gas smell is detected, the system shall be shut down, the main gas valve shall be closed, and the authorized personnel shall be informed.
14. Flammable, explosive, or similar materials shall not be stored in the boiler room.
15. A suitable fire extinguisher shall be kept in the boiler room.
16. The gas detector shall be checked to ensure that it is functioning properly, and periodic maintenance shall be carried out at regular intervals.
17. Smoking is strictly prohibited inside the boiler room.
18. If the heat generation center and the other sections of the workplace where production is carried out are located under the same roof, the heat generation center shall have at least one door opening directly to the outside (street or garden), in addition to the door connecting it to these sections. The doors shall be made of fire-resistant materials.
19. The lighting fixtures in heat generation centers shall be of the vapor-tight type.
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